## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: | Director TMC
Name of Work: | Providing power supply to 60 KVA UPS IN Bio Bank building
Contract No: | TMC/ACTREC/ENGG/ KRS/SQ-20/Power Supply to UPS/2023
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  | HSN Code | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder in Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Supply, installation, testing & commissioning of 3.5core x 50sqmm armoured aluminum cable the following cable on wall/floor/ceiling/structure member or on cable trays or underground, using MS spacers and GI saddles, cable clamp etc. complete in all respect. Cable, conforming to IS: 1554/Part 1/1998, XLPE, Aluminum stranded conductor, armoured, 1100 V class 3.5 x 50 sq. mm A2XFY Aluminum Conductor cable including all fixing accessories | item3 | 185 | Rmt |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2 | SITC of cable Gland 3.5 x 50 sq.mm cable as per tender specifications | item4 | 2 | Each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
3 | SITC of Copper Lugs 25 sq. mm as per tender specifications | item3 | 2 | Each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | SITC of Copper Lugs for 50 sq. mm as per tender specifications | item4 | 6 | Each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
5 | Supply, Installation, Testing and commissioning of 25 mm x 3 mm COPPER strip on surface or in recess for connections including all fixing accessories etc as required | item5 | 50 | Rmt |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | SITC of Tinned copper earth plate electrode 600 x 600 x 3.15 mm earth station, 2.5 mtr below ground level as per drawing complete with all required materials like Cole, charcoal, salt, brass nut bolts & washers, watering arrangements, GI pipe (B class), concrete chamber, heavy duty cast iron cover plate & excavation in all types of soil in ground refilling & removal excess earth within a radius of 500 mtr. Etc. Note:1.The chamber cover & plate shall be of heavy-duty hinged type & it shall weigh approx. 65 to 75 Kgs. For 450 x 450 mm size & shall be got approved by dept. (6 mm chequred plate with 40 x 40 x 6 mm angle iron frame) 2.Plastering shall be done both inside & out side. 3.The measurement of resistance of earth station & resistance of complete scheme of earthing layout shall be measured, recorded & got approved by Engg-in-charge. | item6 | 1 | Each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7 | Supply and fixing of 125A MCCB including metal body enclosure suitable for cable connection of 3.5core x 50sqmm, MCCB 125A , 415volt 3 ph. , 50HZ , TP+N 125 A-36kA MCCB-FROH with cable spreader , Manual, with integral LSIG protection, Rotary operating knob from outside ON OFF , including Phase separator , Protection sheet and including all fixing accessories. | item7 | 2 | Each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
8 | Excavation of hard rock / RCC road cutting as per required 900/1200 mm below ground level including blasting & chiseling, using compressor, dewatering, back filling, if necessary disposal of excess earth within the radius of 500 Mtrs etc. stacking of rocks at selected places as per instruction of EIC. The scope also includes backfilling and final finishing of the excavated length. | item8 | 54.75 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words | [51 empty] | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information